## Daily report
35 TPH SLOP FIRED DPR REPORT
SR.NO | DATE | TIME | FLOW IN TPH |  | FEED WATER | FEED WATER | MS STEAM PR. | MS STEAM TEMP. DEGC | STEAM TEMP | STEAM TEMP | DESUPER HEATING FLOW | FURNACE DRFT. IN MMWC | FSH I/L | PSH I/L | EVAPORATOR I/L | ECONOMISER I/L | SPENT WASH TEMP | SPENT WASH |  | FURNACE TEMP. DEGC | 2nd PASS BEFORE SUPERHEATER | FLUE GAS | FLUE GAS | FLUE GAS | FLUE GAS | O2% | DRAG CHAIN FEEDER RPM% |  |  | BAGASSE FEEDER RPM% |  |  | FD FAN VFD% /RPM | FD AIR FLOW | SA FAN VFD% / RPM | SA AIR FLOW | ID FAN SPEED | AIR PR IN MMWC |  | BAG FILTER FLUE GAS TEMP |  | BAG. FILTER DRAFT. |  | SCAPH O/L TEMP DEGC |  | DEAERATORTEMP IN DEGC. | FUEL CONS. BAGASSE | FUEL CONS. COAL | FUEL CONS. Rice Husk
|  |  | STEAM | FEED WATER | TEMP ECO I/L | TEMP ECO O/L |  |  | (PSH O/L) | (DSH O/L) |  |  | (PSHO/L) | DRFT. IN MMWC | DRFT. IN MMWC | DRFT. IN MMWC |  | FLOW | BRIX |  |  | PSH I/L TEMP | EVAPRATOR I/L | ECO INLET | ECO OUTLET |  | 1 | 2 | 3 | 1 | 2 | 3 | [5 empty] | SA | FD | INLET | OUT LET | INLET | OUT LET | SA FAN | FD FAN | SA | MT | MT | MT
1 | 2020-06-23 | 4:00 | 32.6184 | 34.3474 | 141.5709 | 221.487 | 44.0463 | 399.7416 | 357.3535 | 368.7928 | 0 | -2.0415 | -6.0076 | -15.4978 | -43.2945 | -62.7527 | 66.9919 | 12.5685 | 56.1 | 618.2699 | 488.1281 | 458.0521 | 360.1223 | 341.9031 | 191.0333 | 3.0927 | -0.187 | 0.57299 | 0.046966 | 18.9791 | 21.2037 | 18.6023 | 45.2776 | 24.2002 | 79.2181 | 26.6447 | 78.4833 | 365.0651 | 38.5491 | 191.0333 | 174.0442 | -173.1521 | -360.2549 | 134.1706 | 135.4649 | 141.5709 | 195 | 0 | 0
2 |  | 5:00 | 31.5453 | 34.1799 | 141.6742 | 223.1299 | 43.9441 | 402.1593 | 359.5703 | 371.1033 | 0 | -2.036 | -6.0939 | -15.0601 | -42.5767 | -62.53 | 67.5832 | 12.5928 |  | 620.9913 | 491.7492 | 462.296 | 363.4501 | 344.3593 | 191.5818 | 3.4655 | -0.18635 | 0.57077 | 0.045855 | 17.345 | 19.3704 | 17.0011 | 45.2752 | 24.0345 | 79.2173 | 26.4742 | 78.2879 | 364.5013 | 39.2352 | 191.5818 | 174.1705 | -172.1069 | -360.2586 | 134.7068 | 136.1315 | 141.6742
3 |  | 6:00 | 31.8912 | 33.3476 | 142.0646 | 222.2976 | 44.0697 | 399.8599 | 357.7659 | 369.3735 | 0 | -2.0095 | -5.9446 | -15.3105 | -41.8826 | -60.8949 | 68.7246 | 12.3994 |  | 614.7033 | 489.7599 | 461.3361 | 362.0154 | 342.5442 | 191.288 | 3.3905 | -0.18686 | 0.57405 | 0.044483 | 18.0933 | 20.2317 | 17.7396 | 44.3538 | 23.4723 | 79.4905 | 26.1848 | 77.5245 | 370.1289 | 37.4261 | 191.288 | 173.9421 | -166.1506 | -355.8036 | 135.0514 | 136.6885 | 142.0646
4 |  | 7:00 | 31.3878 | 33.1757 | 141.8238 | 222.5583 | 44.0463 | 401.5152 | 358.8933 | 370.7615 | 0 | -2.013 | -5.657 | -15.0443 | -40.7586 | -59.9192 | 71.499 | 12.5598 |  | 615.7415 | 493.0038 | 464.6564 | 363.8358 | 343.5826 | 191.202 | 3.6157 | -0.18752 | 0.57235 | 0.045629 | 16.4391 | 18.4272 | 16.108 | 44.2695 | 23.2979 | 78.5082 | 25.7267 | 76.7441 | 359.619 | 37.1331 | 191.202 | 174.3103 | -161.6481 | -349.3025 | 135.4994 | 137.0574 | 141.8238
5 |  | 8:00 | 29.1167 | 30.9056 | 143.3593 | 224.4221 | 43.9441 | 403.4473 | 361.0767 | 373.1524 | 0 | -2.0453 | -5.1543 | -13.0713 | -36.2553 | -54.9294 | 76.0513 | 12.5201 |  | 599.614 | 488.2102 | 461.3636 | 362.126 | 341.1542 | 191.3152 | 4.5265 | -0.18487 | 0.57544 | 0.046092 | 14.5281 | 16.2463 | 14.2205 | 45.1423 | 23.5281 | 79.2202 | 25.7144 | 75.027 | 365.4954 | 39.6189 | 191.3152 | 174.3892 | -149.968 | -337.4136 | 135.7296 | 137.112 | 143.3593
6 |  | 9:00 | 32.185 | 33.9187 | 143.1829 | 221.5943 | 44.0697 | 397.5005 | 355.0115 | 367.1188 | 0 | -1.8554 | -4.2256 | -13.4216 | -37.0772 | -56.2385 | 76.8792 | 12.4158 |  | 618.1791 | 497.6617 | 468.9126 | 364.5328 | 343.1037 | 191.7374 | 4.6185 | -0.18447 | 0.57904 | 0.047665 | 16.5829 | 18.5418 | 16.2474 | 45.4068 | 23.4214 | 79.0955 | 25.5742 | 75.8176 | 364.8127 | 39.9372 | 191.7374 | 175.0276 | -152.9528 | -341.727 | 136.2925 | 137.5937 | 143.1829
7 |  | 10:00 | 31.9295 | 34.2923 | 142.8217 | 219.5652 | 44.0463 | 391.7513 | 348.9469 | 361.3363 | 0 | -1.9354 | -4.1323 | -13.8704 | -37.5573 | -56.6054 | 77.544 | 11.7155 |  | 625.2727 | 496.5443 | 462.5712 | 361.5613 | 341.5001 | 191.3946 | 6.4453 | -0.18533 | 0.57671 | 0.048014 | 18.6312 | 20.8274 | 18.2795 | 45.2811 | 23.6324 | 79.2161 | 25.5382 | 76.7138 | 363.1224 | 39.882 | 191.3946 | 174.9733 | -154.0532 | -346.5158 | 136.2309 | 137.6397 | 142.8217
8 |  | 11:00 | 32.8666 | 35.692 | 142.3647 | 212.7478 | 43.9441 | 396.1197 | 348.1301 | 360.4203 | 0 | -1.95 | -4.8899 | -13.6657 | -40.1388 | -58.8782 | 78.377 | 12.4253 |  | 626.964 | 482.4671 | 442.6771 | 347.4498 | 331.101 | 188.787 | 6.745 | -0.187 | 0.5744 | 0.044517 | 20.6268 | 23.0571 | 20.2515 | 45.2766 | 23.3109 | 79.19 | 25.97 | 78.3389 | 354.7379 | 39.5247 | 188.787 | 174.506 | -162.1522 | -355.4282 | 135.5668 | 137.1453 | 142.3647
9 |  | 12:00 | 32.2498 | 34.2221 | 143.0805 | 217.1875 | 44.0697 | 401.5687 | 355.0685 | 367.4135 | 0 | -2.0845 | -5.5003 | -14.6714 | -41.8411 | -59.9357 | 78.8841 | 12.485 |  | 623.6274 | 477.6102 | 443.7455 | 347.462 | 331.4185 | 188.5943 | 6.9605 | -0.18542 | 0.57387 | 0.043145 | 19.2829 | 21.5573 | 18.9127 | 45.281 | 23.6362 | 79.1888 | 26.2265 | 76.9832 | 353.8853 | 39.3446 | 188.5943 | 173.707 | -161.5858 | -345.0756 | 135.4318 | 137.1129 | 143.0805
10 |  | 13:00 | 33.011 | 34.3226 | 142.9054 | 218.1441 | 44.0463 | 400.9921 | 355.2344 | 367.7016 | 0 | -1.802 | -4.7237 | -13.0575 | -41.2446 | -59.4627 | 79.0064 | 12.3835 |  | 625.8961 | 483.882 | 449.4464 | 352.7356 | 335.5848 | 189.9513 | 7.2263 | -0.18235 | 0.57465 | 0.044003 | 18.208 | 20.3728 | 17.8573 | 45.2845 | 23.6011 | 79.186 | 26.3823 | 78.0651 | 355.1425 | 40.3577 | 189.9513 | 173.6419 | -166.7778 | -356.6768 | 135.1797 | 136.9606 | 142.9054
11 |  | 14:00 | 33.5496 | 35.1032 | 142.6227 | 219.5856 | 43.9441 | 403.2914 | 357.6808 | 370.1429 | 0 | -1.9845 | -5.0029 | -13.3681 | -43.2522 | -62.7137 | 79.3053 | 12.3847 |  | 627.902 | 493.8414 | 458.9345 | 359.1939 | 340.9075 | 191.7474 | 7.4366 | -0.18152 | 0.572 | 0.043439 | 18.7529 | 20.9812 | 18.3969 | 45.2874 | 23.942 | 79.1864 | 26.5177 | 79.5779 | 356.5064 | 40.0914 | 191.7474 | 175.9563 | -174.2253 | -364.9644 | 134.7411 | 136.377 | 142.6227
12 |  | 15:00 | 33.5652 | 35.0477 | 143.1236 | 221.5609 | 44.0697 | 405.497 | 359.8856 | 372.4229 | 0 | -1.9095 | -4.3313 | -12.5272 | -43.075 | -62.6133 | 80.1606 | 12.6093 |  | 638.3224 | 500.2776 | 465.9686 | 364.6839 | 344.9452 | 193.4296 | 7.6083 | -0.18223 | 0.57482 | 0.046104 | 18.7608 | 20.9909 | 18.4055 | 45.2833 | 23.7188 | 79.1842 | 26.5742 | 79.8963 | 358.1407 | 40.3853 | 193.4296 | 177.8065 | -175.3928 | -364.6335 | 134.8542 | 136.6472 | 143.1236
13 |  | 16:00 | 33.5419 | 35.2821 | 142.7902 | 222.1693 | 44.0463 | 400.5372 | 356.5479 | 369.0701 | 0 | -2.0361 | -4.2519 | -12.9669 | -42.9646 | -61.9175 | 80.9059 | 12.9054 |  | 633.9444 | 494.2155 | 462.7688 | 363.7845 | 344.6707 | 194.366 | 7.0531 | -0.18362 | 0.579 | 0.046144 | 20.1068 | 22.4853 | 19.7273 | 45.2762 | 23.7492 | 79.191 | 26.562 | 79.8463 | 357.8871 | 40.2313 | 194.366 | 179.1757 | -173.8254 | -361.6748 | 134.8658 | 136.6609 | 142.7902
14 |  | 17:00 | 33.3517 | 35.0828 | 143.1196 | 222.4803 | 43.9441 | 399.9758 | 356.515 | 369.0699 | 0 | -1.8472 | -3.9028 | -14.0066 | -43.9455 | -62.8188 | 81.1176 | 12.8636 |  | 632.0022 | 496.0397 | 465.0055 | 365.6106 | 346.0029 | 194.7634 | 6.9166 | -0.18701 | 0.5806 | 0.045463 | 20.1955 | 22.592 | 19.8154 | 45.2794 | 23.8135 | 79.1852 | 26.5844 | 80.6129 | 357.7113 | 40.0787 | 194.7634 | 179.43 | -176.0433 | -367.6844 | 134.8512 | 136.5797 | 143.1196
15 |  | 18:00 | 33.9173 | 36.4285 | 143.5079 | 222.451 | 44.0697 | 396.5479 | 353.3505 | 366.0173 | 0 | -1.959 | -4.6974 | -14.4083 | -44.9763 | -64.3568 | 80.4245 | 12.0801 |  | 632.4885 | 500.3727 | 468.8138 | 367.5667 | 347.4546 | 195.7756 | 6.9358 | -0.18763 | 0.57559 | 0.0441 | 21.991 | 24.584 | 21.5832 | 45.3692 | 24.4363 | 79.1809 | 26.87 | 80.9576 | 362.7111 | 40.9085 | 195.7756 | 180.1792 | -178.9969 | -367.0571 | 134.2828 | 135.6374 | 143.5079
16 |  | 19:00 | 34.0196 | 36.8059 | 143.4084 | 218.0949 | 44.0463 | 394.3722 | 351.6274 | 364.2448 | 0 | -2.0462 | -4.532 | -12.979 | -44.6609 | -64.477 | 80.2991 | 12.846 |  | 619.3781 | 481.0858 | 452.371 | 352.5483 | 337.0651 | 193.5961 | 6.6331 | -0.18781 | 0.57614 | 0.042933 | 23.7893 | 26.5827 | 23.3511 | 46.5541 | 24.6661 | 77.8687 | 26.4245 | 81.9443 | 351.8115 | 45.4629 | 193.5961 | 180.1284 | -183.7852 | -368.8744 | 134.3519 | 134.1128 | 143.4084
17 |  | 20:00 | 33.9528 | 35.2441 | 144.4084 | 217.6818 | 43.9441 | 391.541 | 350.3619 | 362.8435 | 0 | -1.8665 | -4.8507 | -13.9832 | -43.8279 | -61.8463 | 80.8495 | 12.8634 |  | 612.1374 | 472.7899 | 446.0462 | 348.2049 | 334.0396 | 191.022 | 5.9942 | -0.18566 | 0.57437 | 0.04493 | 23.9066 | 26.7176 | 23.4678 | 44.2707 | 23.2086 | 78.6087 | 26.5576 | 80.4488 | 356.1783 | 39.2567 | 191.022 | 177.3626 | -174.3879 | -365.9329 | 134.508 | 135.598 | 144.4084
18 |  | 21:00 | 33.3918 | 35.0496 | 140.8269 | 220.2603 | 44.0697 | 396.8757 | 355.0884 | 367.462 | 0 | -2.2633 | -5.8709 | -15.4298 | -45.3908 | -62.999 | 81.387 | 12.8517 |  | 610.9893 | 480.5553 | 453.6732 | 354.836 | 338.7719 | 191.8009 | 6.9453 | -0.18623 | 0.6565 | 0.20571 | 23.6177 | 26.3947 | 23.1857 | 45.2819 | 24.1034 | 79.2212 | 26.7574 | 79.879 | 360.0466 | 39.9649 | 191.8009 | 177.9014 | -174.4585 | -363.5508 | 133.8616 | 134.3494 | 140.8269
19 |  | 22:00 | 33.5496 | 35.1189 | 142.6227 | 219.5856 | 44.0683 | 403.2914 | 357.6808 | 371.1482 | 0 | -1.2683 | -5.0029 | -13.3681 | -43.2522 | -62.7137 | 79.3053 | 12.3847 |  | 627.902 | 493.8414 | 458.9345 | 359.1939 | 340.9075 | 191.7474 | 5.7126 | -0.18152 | 0.572 | 0.043439 | 18.7529 | 20.9812 | 18.3969 | 45.2874 | 23.942 | 79.1864 | 26.5177 | 79.5779 | 356.5064 | 40.0914 | 191.7474 | 175.9563 | -174.2253 | -364.9644 | 134.7411 | 136.377 | 142.6227
20 |  | 23:00 | 33.5652 | 35.0615 | 143.1236 | 221.5609 | 44.0463 | 405.497 | 359.8856 | 373.4222 | 0 | -1.1237 | -4.3313 | -12.5272 | -43.075 | -62.6133 | 80.1606 | 12.6093 |  | 638.3224 | 500.2776 | 465.9686 | 364.6839 | 344.9452 | 193.4296 | 7.7363 | -0.18223 | 0.57482 | 0.046104 | 18.7608 | 20.9909 | 18.4055 | 45.2833 | 23.7188 | 79.1842 | 26.5742 | 79.8963 | 358.1407 | 40.3853 | 193.4296 | 177.8065 | -175.3928 | -364.6335 | 134.8542 | 136.6472 | 143.1236
21 |  | 24:00 | 33.5419 | 35.2926 | 142.7902 | 222.1693 | 43.9441 | 400.5372 | 356.5479 | 370.064 | 0 | -1.6144 | -4.2519 | -12.9669 | -42.9646 | -61.9175 | 80.9059 | 12.9054 |  | 633.9444 | 494.2155 | 462.7688 | 363.7845 | 344.6707 | 194.366 | 8.5515 | -0.18362 | 0.579 | 0.046144 | 20.1068 | 22.4853 | 19.7273 | 45.2762 | 23.7492 | 79.191 | 26.562 | 79.8463 | 357.8871 | 40.2313 | 194.366 | 179.1757 | -173.8254 | -361.6748 | 134.8658 | 136.6609 | 142.7902
22 |  | 25:00 | 33.3517 | 35.0977 | 143.1196 | 222.4803 | 44.0697 | 399.9758 | 356.515 | 370.0729 | 0 | -1.2808 | -3.9028 | -14.0066 | -43.9455 | -62.8188 | 81.1176 | 12.8636 |  | 632.0022 | 496.0397 | 465.0055 | 365.6106 | 346.0029 | 194.7634 | 8.3754 | -0.18701 | 0.5806 | 0.045463 | 20.1955 | 22.592 | 19.8154 | 45.2794 | 23.8135 | 79.1852 | 26.5844 | 80.6129 | 357.7113 | 40.0787 | 194.7634 | 179.43 | -176.0433 | -367.6844 | 134.8512 | 136.5797 | 143.1196
23 |  | 26:00 | 33.9173 | 36.4414 | 143.5079 | 222.451 | 43.7857 | 396.5479 | 353.3505 | 366.9967 | 0 | -1.6942 | -4.6974 | -14.4083 | -44.9763 | -64.3568 | 80.4245 | 12.6 |  | 632.4885 | 500.3727 | 468.8138 | 367.5667 | 347.4546 | 195.7756 | 5.6885 | -0.18763 | 0.57559 | 0.0441 | 21.991 | 24.584 | 21.5832 | 45.3692 | 24.4363 | 79.1809 | 26.87 | 80.9576 | 362.7111 | 40.9085 | 195.7756 | 180.1792 | -178.9969 | -367.0571 | 134.2828 | 135.6374 | 143.5079
24 |  | 27:00 | 34.0196 | 36.8157 | 143.4084 | 218.0949 | 43.5423 | 394.3722 | 351.6274 | 365.2227 | 0 | -1.0486 | -4.532 | -12.979 | -44.6609 | -64.477 | 80.2991 | 12.846 |  | 619.3781 | 481.0858 | 452.371 | 352.5483 | 337.0651 | 193.5961 | 3.3571 | -0.18781 | 0.57614 | 0.042933 | 23.7893 | 26.5827 | 23.3511 | 46.5541 | 24.6661 | 77.8687 | 26.4245 | 81.9443 | 351.8115 | 45.4629 | 193.5961 | 180.1284 | -183.7852 | -368.8744 | 134.3519 | 134.1128 | 143.4084
|  |  | 790.0364 | 836.2755 | 3427.2282 | 5293.7596 | 1055.8176 | 9583.5151 | 8533.7158 | 8835.3743 | 0 | -43.7146 | -116.4876 | -332.5959 | -1017.5949 | -1474.7864 | 1868.2033 | 301.6788 | 58.23 | 14980.4615 | 11774.0273 | 11022.5008 | 8635.1081 | 8191.1546 | 4617.0641 | 145.0309 | -4.4487 | 13.8914 | 1.2434 | 473.4334 | 529.3802 | 464.4323 | 1086.5004 | 572.0986 | 1896.9533 | 632.8164 | 1897.9839 | 8622.2715 | 964.5466 | 4617.0641 | 4243.3284 | -4093.9319 | -8627.7172 | 3238.1229 | 3270.8837 | 3427.2282 | 195 | 0 | 0
|  |  | 32.9182 | 34.8448 | 142.8012 | 220.5733 | 43.9924 | 399.3131 | 355.5715 | 368.1406 | 0 | -1.8214 | -4.8537 | -13.8582 | -42.3998 | -61.4494 | 77.8418 | 12.57 | 58.23 | 624.1859 | 490.5845 | 459.2709 | 359.7962 | 341.2981 | 192.3777 | 6.043 | -0.18536 | 0.57881 | 0.051807 | 19.7264 | 22.0575 | 19.3513 | 45.2708 | 23.8374 | 79.0397 | 26.3674 | 79.0827 | 359.2613 | 40.1894 | 192.3777 | 176.8053 | -170.5805 | -359.4882 | 134.9218 | 136.2868 | 142.8012 | 8.125 | 0 | 0
[40 empty] | 340.0465 | 327.2877 | 667.3342
[40 empty] | 339.8161 | 324.2802 | 664.0963
[40 empty] | 340.7628 | 324.8405 | 665.6034
[40 empty] | 339.4671 | 322.738 | 662.2052
[40 empty] | 341.5309 | 326.7823 | 668.3133
[40 empty] | 340.9842 | 326.6974 | 667.6816
[40 empty] | 340.5973 | 326.1818 | 666.7791
[40 empty] | 339.1363 | 326.7514 | 665.8877
[40 empty] | 336.9592 | 326.7293 | 663.6886
[40 empty] | 337.037 | 328.007 | 665.0439
[40 empty] | 337.423 | 328.5674 | 665.9904
[40 empty] | 337.2003 | 328.6603 | 665.8606
[40 empty] | 336.0967 | 325.9885 | 662.0852
[40 empty] | 337.5468 | 329.2862 | 666.833
[40 empty] | 337.4955 | 327.1955 | 664.691
[40 empty] | 339.0612 | 328.425 | 667.4862
[40 empty] | 339.7736 | 324.7618 | 664.5354
[40 empty] | 339.5261 | 323.6886 | 663.2147
[40 empty] | 340.2802 | 324.412 | 664.6921
[40 empty] | 340.225 | 324.218 | 664.4429
[40 empty] | 341.6064 | 326.4812 | 668.0876
[40 empty] | 340.2772 | 324.3018 | 664.579
[40 empty] | 339.2308 | 323.4857 | 662.7165
[40 empty] | 340.1751 | 324.1211 | 664.2962
[40 empty] | 341.7819 | 325.8018 | 667.5837

## Efficiency calculator
c
S.no | Particulars | Data | UOM | Assumptions
1 | Quantity of Slop | 12.57 | TPH | Particulars | Data | UOM
2 | Quantity of Bagasse | 8.125 | TPD | Specific heat of flue gas | 0.23 | kCal/kg°C
3 | Quantity of indian Coal | 0 |  | Specific heat of steam | 0.45 | kCal/kg°C
| Quantity of Imported Coal |  |  | Humidity factor | 0.0204 | (Kg)w/(Kg)a
4 | Quantity of rice husk | 0 |  | Radiation & convection loss | 1.5 | %
| Quantity of fed fuel | 20.695
8 | GCV of Fuel as per fuel quantity | 36875.7761 | Kcal
9 | Flue gas temperature | 192.3777 | °C
10 | Ambient temperature | 31 | °C
11 | Stiochiometric air | 2.532 | Kg/Kg of fuel | FUEL ULTIMATE ANALYSIS
12 | Oxygen in flue gas | 6.043 | %
13 | Excess air | 40.4021 | % | Constituent | Slop | Bagasse | indian coal | Imported coal | Rice husk | Fuel Fed
14 | Actual mass of air | 3.5549 | Kg/Kg of fuel | Carbon | 19.2 | 23.5 | 40.58 | 0 | 36.7 | 20.8929
15 | Actual mass of dry flue gas | 4.9239 | Kg/Kg of fuel | Hydrogen | 2.1 | 3.25 | 1.09 | 0 | 3 | 2.5528
17 | CO in flue gas | 0 | % | Oxygen | 16.5 | 21.75 | 3.5 | 0 | 31.2 | 18.5669
18 | CO2 in flue gas | 0 | % | Sulphur | 1.05 | 0 | 0.5 | 0 | 0.2 | 0.63661
19 | Amount of bottom ash | 20 | TPD | Nitrogen | 1.85 | 1.69 | 0.6 | 0 | 0.9 | 1.787
20 | Unburnt in bottom ash | 5 | % | Moisture | 40 | 50 | 12 | 0 | 10 | 43.937
21 | Amount of fly ash | 2 | TPD | Ratio | 1.54 | 1 | 0 | 0 | 0
22 | Unburnt in fly ash | 15 | %
23 | HEAT LOSS IN DRY FLUE GAS | 10.2534 | % | GCV | 1587.8175 | 2082.0813 | 3515.1765 | 0 | 2659.34 | 1782.4095
24 | HEAT LOSS DUE TO FORMATION OF WATER FROM H2 IN FUEL | 8.4637 | %
25 | HEAT LOSS DUE TO MOISTURE IN FUEL | 16.1859 | % | Stoichiometric air | 2.2859 | 2.9109 | 4.9561 | 0 | 3.9527 | 2.532
26 | HEAT LOSS DUE TO MOISTURE IN AIR | 0.40925 | %
27 | HEAT LOSS DUE TO PARTIAL COMBUSTION | 0 | %
28 | HEAT LOSS DUE TO RADIATION AND CONVECTION | 1.5 | %
29 | HEAT LOSS DUE TO UNBURNT IN BOTTOM ASH | 4.5332 | %
30 | HEAT LOSS DUE TO UNBURNT IN FLY ASH | 1.36 | %
31 | TOTAL LOSSES | 42.7054 | %
32 | EFFICIENCY BY INDIRECT METHOD | 57.2946 | % | INDIRECT (ᶯ) | 57.2946 | %
BY AWAKE CHAUDHARY
|  |  |  | DIRECT (ᶯ) | 54.8327 | %
33 | Quantity of steam | 32.9182 | TPH | [5 empty] | https://www.linkedin.com/in/awake-chaudhary-741006146/
34 | Feed water temp. | 142.8012 | °C | Efficency difference | 2.4619 | %
35 | Enthalpy of feed water | 151 | Kcal/kg
36 | Generated Steam temp. | 399.3131 | °C | Fuel imbalance with respect to bagasse | 0.34912 | TPD
37 | Generated Steam pressure | 43.9924 | Kg/cm2
38 | Enthalpy of steam | 765.25 | Kcal/kg
39 | EFFICIENCY BY DIRECT EFFICIENCY | 54.8327